[image: ]The Head Office,
People’s Primary Healthcare Initiative, Balochistan.
Admin Section
Ref No. PPHI-B/H.O-BLN/SOLAR/2026-27/01
Dated: 	

Technical Proposal
People’s Primary Healthcare Initiative (PPHI) - Balochistan

Bidding Document for Supply, Installation and commissioning of Solar Step-Up Systems at 157 Basic Health Units (BHUs), Across Balochistan.




NAME OF BIDDER: 	
(To be filled-in by the Bidder)








Address:	People’s Primary Healthcare Initiative (PPHI) – Balochistan House # 8-A, Jinnah Town Samungli Road, Quetta-Pakistan.
Phone:	081-2863620
Website:	www.pphib.org
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LETTER OF INVITATION FOR BIDS:
Sealed proposals are invited under the People’s Primary Healthcare Initiative (PPHI-Balochistan) from eligible, qualified, and PEC-registered firms having relevant expertise in the design, supply, installation, testing, and commissioning of solar power systems on a free delivery, installation, and commissioning at consignee’s end basis.

	
REQUIRED BIDDING INFORMATION
	
TO BE FILLED BY THE PEOPLES PRIMARY HEALTHCARE INITIATIVE (PPHI-B)

	
DESIGNATION OF PROCUREMENT OFFICER
	
DIRECTOR  ADMIN & PROCURRENT 

	POSTAL ADDRESS OF THE PEOPLE’S PRIMARY HEALTH CARE INITIATIVE (PPHI-BALOCHISTAN)
	HOUSE # 8-A, JINNAH TOWN SAMUNGLI ROAD, QUETTA-PAKISTAN.

	PHONE NUMBER & FAX NUMBER
	081-2863620 & 081-2863623

	E-MAIL ADDRESS &WEBSITE
	E-mail: PPHIBLN@GMAIL.COM
Website: https://www.pphib.org

	METHOD OF PROCUREMENT
	OPEN COMPETITIVE BIDDING

	BIDDING PROCEDURE
	SINGLE STAGE - TWO ENVELOPE BIDDING PROCEDURE

	EVALUATION MECHANISM
	ELIGIBILITY & RESPONSIVENES:
BIDS SHALL BE EVALUATED ON A PASS/FAIL BASIS. ONLY BIDDERS MEETING ALL MANDATORY ELIGIBILITY CRITERIA (“YES” AGAINST EACH REQUIREMENT) SHALL BE DECLARED RESPONSIVE.
FINANCIAL EVALUATION & AWARD:
FINANCIAL PROPOSALS OF RESPONSIVE BIDDERS SHALL BE OPENED AND EVALUATED. THE CONTRACT SHALL BE AWARDED LOT-WISE TO THE LOWEST
EVALUATED RESPONSIVE BIDDER FOR EACH RESPECTIVE LOT.

	EVALUATION TYPE
	LOT-WISE

	PRE-BID MEETING
	DATE: 21th Sep 2026 AT 2:00 P.M, PPHI-B HEAD OFFICE, 8-A JINNAH TOWN, SAMSUNGLI ROAD, QUETTA. ALL COMPETITIVE BIDDERS ARE REQUESTED TO ATTEND THE PRE BID MEETING.

	ISSUANCE OF BIDDING DOCUMENTS
	The tender documents can be downloaded from the PPHI- Balochistan website: http://pphib.org/

	DEADLINE FOR SUBMISSION OF BIDS
	Date: 30th September 2026 & Till 11:00 A.M directly submitted to the Head Office, PPHI-Balochistan.

	OPENING OF TECHNICAL BIDS
	Date: 30th September 2026 & Time 12:00 P.M at the Head Office of PPHI-Balochistan.

	OPENING OF FINANCIAL BIDS
	Date: Shall be communicated to qualified bidders after technical evaluation.

	BIDDING DOCUMENT FEE
	AMOUNT: PKR. 2,000/- PAY ORDER IN THE NAME OF PPHI- Balochistan WITH TECHNICAL BID IN A SEPARATE ENVELOPE. SUBMISSION OF BIDDING DOCUMENT FEE IS MANDATORY WITH TECHNICAL PROPOSAL, IT WILL BE
CHECKED DURING THE ELIGIBILITY ASSESSMENT.

	BID SECURITY/EARNEST MONEY
	AMOUNT: 2% OF THE QUOTED AMOUNT MANNER OF PAYMENT: CALL DEPOSIT/ PAY ORDER IN FAVOR OF PPHI-BALOCHISTAN, WITH FINANCIAL
PROPOSAL



	PERFORMANCE SECURITY (WARRANTY)
	2% CDR SHALL BE RETAINED AS PERFORMANCE SECURITY FOR THE WARRANTY PERIOD. THE AMOUNT SHALL BE RELEASED UPON SATISFACTORY
COMPLETION OF THE WARRANTY PERIOD.

	SCOPE OF BIDDING
	NATIONAL

	BID VALIDITY PERIOD (DAYS)
	60

	JV-CONSORTIUM ALLOWED
	NO



ELIGIBILITY CRITERIA FOR BIDDERS:

	
SR. NO
	BIDDERS ELIGIBILITY FACTOR
	
MANDATORY REQUIREMENT
	
DOCUMENT REQUIRED

	




01
	



Legal Status & Tax Registration
	Bidder must have valid registration with following Government Departments
i. Relevant Tax authorities i.e. for Income Tax (NTN) and Sales Tax Registration. Must be on active taxpayer list of FBR.
ii. PEC Registration Category C-6 or above with relevant specialization code EE-11 / RE (Solar/Renewable Energy/Solar Installation)
iii. Balochistan Revenue Authority (must have valid registration.
	
a) Copy of Income Tax and sales Certificate.
b) Copy of registration with Pakistan Engineering Council.
c) Copy of Registration Certificate with Balochistan Revenue Authority

	

02
	
Relevant Experience
	The bidder must have successfully completed up to five (05) similar assignments during the last three financial years (FY-2024, FY-2025, and FY-2026), with a total contract value of not less than PKR 20 million.
	Copy/ies of Work Order/s and relevant completion certificate/s, where quantities & amount are clearly mentioned duly attested by Senior Executive of the firm.

	03
	Financial Capacity (For Firms)
	The bidder must have an average annual turnover of not less than PKR 10 million during the last three financial years (FY-2024, FY-2025, and FY-2026).
	Audited	Financial	Statements	OR Annual Tax Return only.

	
04
	Non-Blacklisting and disclosure of litigation cases
	Must not be presently black-listed by any Government/ Semi Govt or Private Organization must disclosed the litigation cases.
	Declaration of Non-blacklisting and disclosure of litigation cases on Non- Judicial   Stamp   paper   by   the
Bidder/Individual.

	
05
	Delivery time compliance
	Must agree to serve the Contract within agreed time i.e., Within  45 days period after award of
Work Order.
	Written acceptance must be provided in the Technical Bid in letter head of the Firm/Company.

	

06
	
Agreement with all the terms & conditions
	Must unconditionally agree with all the instructions, terms & conditions specified in the bidding documents & contract agreement.
	Signature & company seal on every page of the bidding document and/or declaration by the bidder on the firms letter pad to agree with all terms and
conditions.

	


07
	

Submission of Tender Fee & Security Deposit
	

As required by the Peoples Primary Healthcare Initiative (PPHI-B) in the Tender Notice.
	AMOUNT: PKR. 2,000/- Tender Fee in separate envelope with technical proposal.
AMOUNT: Bid Security equivalent to 2% of total quoted bid price in shape of Pay Order/CDR/Demand Draft in favor of PPHI-B with Financial Proposal only

	


08
	

Submission of Separate Bid for Each Lot
	

The bidder shall submit a separate and complete bid for each lot.
	Bidders intending to participate in more than one lot shall submit a separate and complete bid for each lot, clearly marked and sealed independently. Evaluation and award shall be conducted lot-wise, and each lot shall be
treated as a separate contract.

	

09
	
Submission of Technical Specifications
	The bidder shall submit detailed technical specifications on official letter head of the firm as required under Specific Data/Work Sheet
	The bidder shall also attach relevant brochures, catalogues, and/or manufacturer’s data sheets for each
quoted item, clearly indicating compliance   with   the   specified
requirements. All documents shall be submitted  as  part  of  the  technical
proposal for evaluation purposes.

	
  10
	Minimum Warranty Undertaking
	Bidder must provide warranty undertaking on firm letter head clearly specifying standard warranty period for solar panels, inverters and batteries.
	Undertaking on firm letter head specifying standard warranty period with technical proposal




NOTE:
a) It is mandatory for the bidders to score “YES” in all the above-mentioned Ten (10) requirements of eligibility. In-case of single “NO” to any requirement, the Bid shall be declared NON-RESPONSIVE resulting disqualification for sample submission and financial bid opening.
b) No document shall be added in bidding documents once bid documents are submitted.
c) Submission of Multiple Bids under a Single Firm (Lot-wise):
i. A Single Bidders may be awarded multiple lots, subject to fulfillment of technical and financial qualification criteria. 
ii. Each bid shall be complete in all respects and shall be submitted separately, including independent Technical and Financial Proposals along with a separate Call Deposit Receipt (CDR)/Bid Security for each lot. Partial bidding within a lot or submission of incomplete bids shall render the bid non- responsive.
d) Please avoid to attach documents not required in the above mentioned criteria and it would be convenient to tag each eligibility criteria documents.
e) Bidders from other cities/provinces may send their bids via courier at below mentioned mailing address and can participate in the bidding process virtually through online link (subject to prior intimation to the procuring officer) if desired, otherwise physical presence is preferred.
f) The Procuring Agency reserves the right to reject any or all bids or cancel the procurement proceedings at any time prior to award of contract.

Postal Address: PPHI-B Head Office House # 8-A, Jinnah Town, Samungli Road, Quetta.











Method of Procurement:
Single Stage Two Envelope Procedure
i. Bid shall comprise of a single package containing two separate envelopes. Each envelope shall contain separately the financial proposal and the technical proposal
ii. Envelopes shall be marked  as “FINANCIAL PROPOSAL” and “TECHNICAL PROPOSAL” in
bold and legible letters to avoid confusion;
iii. Initially, only the envelope marked “TECHNICAL PROPOSAL” shall be opened;
iv. Envelope marked as “FINANCIAL PROPOSAL” shall be retained in the custody of
The procuring agency without being opened;
v. Procuring agency shall evaluate the technical proposal in a manner prescribed in given “Bid Evaluation Criteria” in the bidding document, without reference to the price and reject any proposal which does not conform to the specified requirements;
vi. No amendments in the technical proposal shall be permitted after submission of technical and finical proposal;
vii. Financial proposals of technically qualified bids shall be opened publicly at a time, date and venue announced and communicated to the bidders by procuring agency.
viii. Financial proposal of bids found technically non-responsive shall be returned unopened to the respective bidders; and
ix. Bid found to be the lowest evaluated shall be accepted. 
Bidding Instructions and General Conditions

1. Bid Submission Requirements
a) The bidder must quote for the entire scope of works specified in the tender document in each Lot. Partial, conditional, or incomplete bids shall be rejected.
b) All bids must be tape-bound, properly sealed, and clearly labeled. Each page must be numbered, signed, and stamped by the authorized representative of the firm.
c) All documents shall be attached in the sequence prescribed in the tender document for evaluation purposes.
d) Any interlineations, erasers, or overwriting shall be valid only if initialized by the person(s) signing the bid.
e) Blank fields in the bid forms must be duly filled. Incomplete or unsigned bids shall be treated as non- responsive.
2. Total Scope of work Requirement
a) Prices must be quoted for the entire scope of works of (Lot) to be executed as specified in the tender document, including all designated sites, locations, and work components.
b) Partial, multiple, conditional, or alternative offers, such as quoting only for selected works, locations of the lot, or components, shall be considered non-responsive and rejected.
3. Method and Deadline of Submission
a) Preferably, bids shall be submitted by hand through the firm’s authorized representative on or before the date and time specified in the Letter of Invitation. Bidders from other provinces may dispatch their bids via courier to the address mentioned below. Such bidders may also participate in the bid opening proceedings virtually through an online link, subject to prior intimation to the Procuring Officer. Physical presence of bidders or their representatives is preferred.
b) The bid shall comprise a single package containing two separate envelopes: a.Technical Proposal
b.Financial Proposal
c) Each envelope shall be sealed and marked in bold letters as “TECHNICAL PROPOSAL” and “FINANCIAL PROPOSAL” (in case of bidding for more than one lot)
d) Both envelopes shall then be placed in an outer sealed envelope clearly marked with the Tender Reference Number and Subject.
e) Bids received after the specified deadline shall be rejected without opening.
4. Conditions for Opening and Validity
a) If the submission or opening date falls on a public holiday or non-working day, the bids shall be opened on the next working day at the same time and venue.
b) A bidder may withdraw its bid before the submission deadline.
I. No withdrawal is permitted after the submission deadline until the expiry of the bid validity period.
II. Any withdrawal during the validity period may lead to legal action under applicable rules of PPHI-B.

5. Eligibility of Bidders
a) The invitation is open to all firms registered with the Federal Board of Revenue (FBR) under the relevant registration/tariff category for Power & Energy / Solar / Government Contractors, subject to fulfillment of all mandatory eligibility criteria.
b) Bidders must have demonstrated experience in the execution and completion of such nature work for government, semi-government, institutional, or similar organizations.

c) Bidders under declaration of ineligibility, suspension, or blacklisting by any government, regulatory authority, or other organization are not eligible to participate.
6. Blacklisting and Debarment
The following actions shall render a bidder liable for blacklisting/debarment:
a) Submission of false, fabricated, or forged documents or misrepresentation of facts at any stage of the bidding or contract execution.
b) Failure to execute the works in accordance with the approved technical specifications, quality standards, BOQs, or agreed completion schedule.
c) Persistent non-compliance with contract terms or specifications.
d) Engagement in corrupt, fraudulent, or unethical practices.
e) Bid rigging, tender fixing, or any conduct detrimental to the integrity and transparency of the procurement process.
f) Any security-related concerns or actions that adversely affect the reputation of the Procuring Agency or the State.
7. Clarifications and Amendments
a) A prospective bidder may seek clarification(s) in writing not later than seven (7) days prior to the submission
deadline at the Procuring Agency’s address indicated in the Bid Data Sheet.
b) The Procuring Agency shall issue written responses (without disclosing the identity of the inquirer) to all bidders who have obtained the documents no verbal response shell be accepted.
c) The Procuring Agency may, at any time before the submission deadline, amend the bidding documents through a written addendum.
d) Such amendments shall be notified through official correspondence (letter, email, fax) or publication on the official PPHI-B website.
e) To accommodate the amendment(s), the Procuring Agency may extend the bid submission deadline, if deemed necessary.
8. Corrupt or Fraudulent Practices and Mechanism for Debarment / Blacklisting
A. Definition of Corrupt and Fraudulent Practices
For the purpose of this tender, the following practices shall constitute corrupt, fraudulent, coercive, collusive, or obstructive behavior, which are strictly prohibited:
a) Corrupt Practice: Offering, giving, receiving, or soliciting directly or indirectly anything of value to influence the actions of a public official, procuring entity, or any party in the procurement process or contract execution for wrongful gain.
b) Fraudulent Practice: Any act, omission, or misrepresentation that knowingly or recklessly misleads or attempts to mislead another party to obtain undue advantage or avoid an obligation.
c) Collusive Practice: Any agreement or arrangement between two or more parties designed to establish bid prices at non-competitive, artificial levels to the detriment of fair competition.
d) Coercive Practice: Direct or indirect actions, threats, or harm to any party or its property to improperly influence their participation or decisions in the procurement process.
e) Obstructive Practice: Deliberate acts intended to impede investigation or audit processes, including falsifying or concealing evidence, making false statements, or intimidating witnesses.

9. Bid Price
a) Price Indication: The bidder shall indicate, in the prescribed form, the unit rates (where applicable), BOQ rates, and the total bid price.
b) Completion and Authentication: The Bill of Quantities (BOQ) and price schedules must be carefully filled, preferably typed, and signed and stamped on each page by the authorized representative of the bidder.
c) Compliance with Technical Specifications: Bids must comply with all approved technical specifications, and BOQ requirements. Any deviation shall render the bid non-responsive.
d) Inclusive Pricing: Prices must be quoted on a complete execution basis and shall include all applicable taxes, duties, levies, transportation, site establishment, tools and incidental costs necessary for execution of the works at the designated Sites of PPHI-Balochistan.
e) Tax Exemptions: Any exemption or reduction in taxes or duties available under law shall be passed on to the Procuring Agency.
f) Total Service Requirement: Prices must be quoted for the entire scope of work of each lot as defined in the tender documents. Partial, conditional, or incomplete offers shall be considered non-responsive and rejected.
10. Bid Security
The bidder shall submit a bid security amount equal to 2% of the total quoted bid price for each lot, in favor of PPHI-Balochistan. The bid security shall be submitted as part of the Financial Bid only.
11. Bid Validity
a. Bids shall remain valid for 60 days from the date of technical bid opening.
b. Bidders agreeing to extend validity must not change the substance of their bids.
c. Bidders declining to extend may withdraw without forfeiting bid security.

Bidders who:-
a) Agree to the Procuring Agency’s request for extension of bid validity period shall not be permitted to
change the substance of their bids; and
b) Do not agree to an extension of the bid validity period shall be allowed to withdraw their bids without forfeiture of their bid securities.
12. Sub-Contracting, Subletting Clause
The bidder shall not assign, transfer, or sublet the whole or any part of the contract without the prior written approval of the Procuring Agency to subcontractor.
Any subletting or subcontracting carried out without such approval shall constitute a material violation of the Contract and shall render the Contractor liable to termination of the Contract, forfeiture of Performance Security, blacklisting, and any other action permissible under the prevailing procurement rules and laws.
(Mailing Address: PPHI-B Head Office House # 8-A, Jinnah Town, Samungli Road, Quetta.)

BIDDER’S INFORMATION: (To be filled-in by the Bidder)

1. Name of company/Individual:	

2. Complete Postal Address:	




3. Tel No:	4. Email address:	


5.	Fax No: 	6. Mobile No: 	


7. Authorized Representative’s name & designation:



8. Type of Business:
(1) Sole Proprietorship	□	(2)	Partnership	□
(3)	Corporation (Private Ltd.) □	(4)	Corporation (Public Ltd.) □

9. National Tax Number& Date of issuance: _	

10. Sales Tax Registration No.	


11. Bid Validity 	(Please specify in no. of days)


12. Total Completion Time	(Date of completion)

DELIVERY SCHEDULE CONDITIONS

1. Scope of Delivery & Locations
The successful bidder shall be responsible for the execution and completion of all work in accordance with the approved technical specifications, and Bill of Quantities (BOQ) at the designated sites of PPHI- Balochistan as specified in the Tender Document.
2. Completion Time & Work Schedule
A) Contract Period
a. The successful bidder shall complete execution of all work at the designated sites of PPHI- Balochistan within 45 (forty five) days from the date of issuance of the Work Order.
b. Works shall be carried out strictly in accordance with the approved work schedule, unless an extension is granted in writing by PPHI-Balochistan.
B) Phased Based Execution
a. Phased or milestone-based execution may be permitted only with prior written approval of PPHI-Balochistan.
b. Each approved phase/milestone shall remain within the overall contract period of 90 days.
C) Execution & Progress Documentation
The bidder shall submit:
· Work Completion Certificates
· Final Completion Report duly signed by the Engineer / Authorized Representative of PPHI- Balochistan
D) Penalty for Delay
Delay beyond the stipulated 45-day period, excluding delays approved in writing or arising from force majeure, shall attract liquidated damages at the rate of 0.25% per day of the value of the uncompleted portion of works, subject to a maximum of 10% of the total contract value.
E) Force Majeure
Delays caused by events beyond the bidder’s control, including natural disasters, civil disturbances, acts of government, strikes, or other force majeure circumstances, must be immediately reported in writing to PPHI-Balochistan with supporting evidence. A reasonable extension may be granted at the discretion of PPHI-Balochistan.
F) Defects, Damages & Loss
The bidder shall be fully responsible for any damage, defects, poor workmanship, or loss occurring during execution of the works. Any defective or non-compliant work shall be rectified or replaced at the bidder’s cost, or the equivalent cost shall be deducted from the payable amount, as determined by PPHI- Balochistan.

3. Place & Mode of Execution
The successful bidder shall be solely responsible for the mobilization of all materials, equipment, and manpower to the designated work sites as specified in the tender documents. The bidder shall ensure safe execution, completion, and handover of the works in strict accordance with the approved technical specifications, and applicable standards.

The bidder shall also provide all required tools, plant, safety gear, and qualified technical staff necessary for proper execution of the works. All arrangements relating to site establishment, storage, handling of materials, safety, and execution logistics shall be the sole responsibility of the bidder.
4. Equipment & Site Handling Requirements
The Bidder must ensure:
a. Availability of appropriate equipment, machinery, and tools required for timely and quality execution of the works.
b. Proper storage, protection, and handling of materials to prevent damage, deterioration, or misuse.
5. Monitoring & Reporting
The Bidder shall:
a. Provide regular progress updates and reports as required by PPHI-Balochistan.
b. Immediately report any delay, accident, defect, or incident affecting the execution of works.
c. Submit Final Completion Confirmation duly acknowledged by the Engineer / Authorized Representative of PPHI-Balochistan.

SCOPE OF WORK AND DATA-SHEET OF THE ASSIGNMENT SCOPE OF WORK:
The scope of work shall comprise the design, supply, installation, testing, and commissioning of complete solar power systems at various locations across Balochistan under the People’s Primary Healthcare Initiative (PPHI-Balochistan), including Basic Health Units (BHUs), District Offices (DOs), and the Head Office.
The required system capacities are as follows:
· 2.6 kVA Solar Power System for Basic Health Units (BHUs)
The successful bidder shall be responsible for conducting site assessments, system design, supply of all required components, installation, wiring, mounting structures, protection systems, testing, commissioning, and handover of fully operational systems.
All materials, equipment, and components shall be procured from recognized and reputable manufacturers and must strictly comply with the technical specifications, standards, and certifications prescribed in the bidding documents. No refurbished or substandard equipment shall be accepted.
The bidder shall ensure that the installed systems are complete in all respects and capable of delivering the required performance in accordance with the approved technical criteria.

DATA SHEET:
The objective of this Data Sheet / Schedule of Requirements is to provide bidders with
comprehensive and clear information to fully understand the complete scope of this Work. It ensures that all requirements of the People’s Primary Healthcare Initiative (PPHI-Balochistan) related to the execution, materials, workmanship, timelines, and delivery of works are clearly defined, specified, and duly incorporated, leaving no requirement unaddressed.
               Lot-wise List of Sites (Requirement 2.6 kVA Solar Complete System) – PPHI-Balochistan
	Lot No.
	District 
	No.Site
	S.No
	Location/Name of BHUs 

	1
	Musakhail 
	10
	1
	BHU Zimri Beer

	
	
	
	2
	BHU Baloch Khusta

	
	
	
	3
	BHU Wah Hassan Khail

	
	
	
	4
	BHU Alam Din Malezai

	
	
	
	5
	BHU Zahir Shah

	
	
	
	6
	BHU Elahi Bux

	
	
	
	7
	BHU Hafiz Toor Khan

	
	
	
	8
	BHU Andarvehi  Sheikhan

	
	
	
	9
	BHU Alam Khan

	
	
	
	10
	BHU Allah Dad Malalzai

	
	Upper Dera Bugti
	5
	1
	BHU Washian

	
	
	
	2
	BHU Imam Bux

	
	
	
	3
	BHU Khairo

	
	
	
	4
	BHU Ghualm Rasool

	
	
	
	5
	BHU Zahid Ali Choto Konal

	
	Barkhan
	7
	1
	BHU Ahmed Baskhash Balwani

	
	
	
	2
	BHU Saeed Abad

	
	
	
	3
	BHU Nikaari

	
	
	
	4
	BHU Lohma Zaireen

	
	
	
	5
	BHU Behdiani

	
	
	
	6
	BHU Hsaaan Shah

	
	
	
	7
	BHU Wadera Hassan 

	
	Kohlu
	8
	1
	BHU Mir Hamza Langani

	
	
	
	2
	BHU Mir Zamuran

	
	
	
	3
	BHU Khalid Mehmood

	
	
	
	4
	BHU Sanaullah Kungerani

	
	
	
	5
	BHU Khalil Soobazai

	
	
	
	6
	BHU Thadri

	
	
	
	7
	BHU Mir Sarang Abad Sonari

	
	
	
	8
	BHU Juma Khan Kalwani

	Total Number of Sites in Lot 1
	30
	 
	 

	Lot No.
	District 
	No.Site
	S.No
	Name of BHUs 

	2
	Awaran
	24
	1
	BHU Shandi

	
	
	
	2
	BHU Goko Laksar

	
	
	
	3
	BHU Arah

	
	
	
	4
	BHU Waja Bhag

	
	
	
	5
	BHU Koto

	
	
	
	6
	BHU Garai

	
	
	
	7
	BHU Gilli

	
	
	
	8
	BHU Kalathoo

	
	
	
	9
	BHUKohro

	
	
	
	10
	BHU Dam Ali Muhammad

	
	
	
	11
	BHU Zoomdan Pirunder

	
	
	
	12
	BHU Kahn e Zeeing

	
	
	
	13
	BHU Kalaro

	
	
	
	14
	BHU Teertij

	
	
	
	15
	BHU Cherry Malar

	
	
	
	16
	BHU Sham Mara

	
	
	
	17
	BHU  Gushunag

	
	
	
	18
	BHU Hore

	
	
	
	19
	BHU Manguli

	
	
	
	20
	BHU Parwar

	
	
	
	21
	BHU Laaki

	
	
	
	22
	BHU Jebri

	
	
	
	23
	BHU Nagago

	
	
	
	24
	BHU Dhal Bedi

	Total Number of Site in Lot 2
	24
	 
	 

	Lot No.
	District 
	No.Site
	S.No
	Name of BHUs 

	3
	Killa Saifullah
	3
	1
	Killi Noor Muhammad Nasar Samkhail Muslim Bagh 

	
	
	
	2
	Kach Mandokhail 

	
	
	
	3
	Killi Akhundzada Aman Ullah 

	
	Loralai
	7
	1
	Killi Malik Sanzar Khan Dealy.

	
	
	
	2
	Malik Abdul Hakeem Zara Nala Malazai.

	
	
	
	3
	Dargai Sargara

	
	
	
	4
	Malak Naseebullah Nigang

	
	
	
	5
	Ghulam Dastageer

	
	
	
	6
	Sardar Muhammad Killi Shakhi Makhter

	
	
	
	7
	Khalaq Zakhpail Dargai Zakhpail

	
	Duki
	3
	1
	BHU Muhammad Akabr Machi

	
	
	
	2
	BHU Dahkhi  Nasur Ullah Khan

	
	
	
	3
	Killi Saif Ullah Jan Din Meh Killa Thal

	Total Number of Site in Lot 3
	13
	 
	 

	Lot No.
	District 
	No.Site
	S.No
	Name of BHUs 

	4
	Quetta
	1
	1
	BHU Randozai Aghbargi

	
	Chagai
	1
	1
	BHU killi Malik Shair Khan Karoduk

	
	Kharan
	1
	1
	BHU Qadir Abad

	
	Barshor
	2
	1
	BHU Kut

	
	
	
	2
	BHU Killi Zar Kach

	
	Pishin
	7
	1
	BHU Killi Qasim 

	
	
	
	2
	BHU Yaro

	
	
	
	3
	BHU Killi Abdullah Jan

	
	
	
	4
	BHU Thrata

	
	
	
	5
	BHU Muchan

	
	
	
	6
	BHU Killi Mandon

	
	
	
	7
	BHU ismailzai

	
	Killa Abdullah
	10
	1
	BHU Killa Ahmad Khan (164 BHUs)

	
	
	
	2
	BHU Tash Dobandi (164 BHUs)

	
	
	
	3
	BHU Mana Jalezai (164 BHUs)

	
	
	
	4
	BHU Juma Khan Aghbarg Dobandi (164 BHUs)

	
	
	
	5
	BHU Noor Muhamad Aghbarg Dobandi (164 BHUs)

	
	
	
	6
	BHU Qasim Bagh

	
	
	
	7
	BHU Adamzai Segai

	
	
	
	8
	BHU Haji Khudae Raheem

	
	
	
	9
	BHU Killi Amin New Majak

	
	
	
	10
	BHU Choor Masezai

	
	Chaman
	3
	1
	BHU Haji Muhammad Ali Pelwan Sui Karez Chaman

	
	
	
	2
	BHU Malik Muhammad Jan

	
	
	
	3
	BHU Daulat Abad Sui Karez Chaman

	
	Ziarat
	3
	1
	BHU Porana Sanjavi

	
	
	
	2
	BHU Inzargat Sanjavi

	
	
	
	3
	BHU Gorasthin Mana

	Total Number of Site in Lot 4
	28
	 
	 

	Lot No.
	District 
	No.Site
	S.No
	Name of BHUs 

	5
	Mastung
	2
	1
	BHU Kandaw

	
	
	
	2
	BHU Muhammad Waris

	
	Surab
	4
	1
	BHU Killi Khiazi Jeewa

	
	
	
	2
	BHU Matt Sanari

	
	
	
	3
	BHU Chhad  Meraji

	
	
	
	4
	BHU Shakar Dann

	
	Khuzdar 
	10
	1
	BHU Trasani Zehri

	
	
	
	2
	BHU Hassan Abad Baghbana

	
	
	
	3
	BHU Khad Shar Baghbana

	
	
	
	4
	BHU Chuta Karkh

	
	
	
	5
	BHU Jhalaro Karkh

	
	
	
	6
	BHU Saraab  Sasool 

	
	
	
	7
	BHU Gouro Sasool

	
	
	
	8
	BHU Banu Bhat Zeedi

	
	
	
	9
	BHU Drawkalaw

	
	
	
	10
	BUH Gohrawa Baghbana

	
	Kalat
	    15
	1
	BHU Chotank Malangzai

	
	
	
	2
	BHU Dinganzai Mamangzai

	
	
	
	3
	BHU Korki Salarzai

	
	
	
	4
	BHU Purduzai

	
	
	
	5
	BHU Sor Jamndzai

	
	
	
	6
	BHU Koor Aadmzai

	
	
	
	7
	BHU Neemargh

	
	
	
	8
	BHU Killi Mubarak Johan

	
	
	
	9
	BHU Malghuzar

	
	
	
	10
	BHU Kohing

	
	
	
	11
	BHU Killi Rahim abad Kohaing

	
	
	
	12
	BHU Yousufzai 

	
	
	
	13
	BHU Haji Hadir Khan Zarzai

	
	
	
	14
	BHU Killi Khuda Buxzai

	
	
	
	15
	BHU Chori Baqa Jalalzai

	Total Number of Site in Lot 5
	     31



	Lot No.
	District 
	No.Site
	S.No
	Name of BHUs 

	6
	Gwader
	6
	1
	BHUSirdasht/Nokebur

	
	
	
	2
	BHU Chakkuli

	
	
	
	3
	BHU Shatangi

	
	
	
	4
	BHU Kandasol

	
	
	
	5
	BHU Saiji

	
	
	
	6
	BHU Faqeer abad

	
	Kech
	4
	1
	BHU Solo and Residential Quarter

	
	
	
	2
	BHU Bunap

	
	
	
	3
	BHU Kohak Dasht

	
	
	
	4
	BHU Baloor

	
	   Washuk
	2
	1
	BHU Gwaragi

	
	
	
	2
	BHU Daali 

	
	Panjgur
	3
	1
	BHU Khar Putt Essai

	
	
	
	2
	BHU Dazi

	
	
	
	3
	BHU Soruk 

	Total Number of Site in Lot 6
	     15



	Lot No.
	District 
	No.Site
	S.No
	Name of BHUs 

	7
	Naseerabad
	4
	1
	Peer Muhammad Mengal

	
	
	
	2
	BHU Shakar Khan Jatak 

	
	
	
	3
	BHU Ranjhan Khan Hara

	
	
	
	4
	BHU Ameer Baksh Mengal

	
	Jaffarabad
	4
	1
	BHU Sakhi Azizullah Badini

	
	
	
	2
	BHU Noor Muhmmad 

	
	
	
	3
	BHU Turkish Colony Dera Allah Yar

	
	
	
	4
	BHU Mustafa Lehri

	
	Jhal Magsi
	4
	1
	BHU Safarani

	
	
	
	2
	BHU Zulfiqar Abad

	
	
	
	3
	BHU Safiabad

	
	
	
	4
	BHU Yadgar

	
	Shobat Pur
	1
	1
	BHU Adil Bugti

	
	Dera Bugti
	3
	1
	BHU Killi Shahzad ( Peshbogi)

	
	
	
	2
	BHU Sher Dil Karmazai

	
	
	
	3
	BHU Wadera Meer Muhammad Shaheed

	Total Number of Site in Lot 7
	
      16
 


	Note: 
I. However the number of sites in each lot can be increased or decreased at any stage of the process.
II. The Procuring Agency reserves the right to change the site/location of the work within the same district, provided that the scope of work and the contract value remain unchanged.

	
        SPECIFIC WORKS DATA
· Bidders shall fill specifications of offered products in the following table.
· Write “compliance” if same specifications are offered and for non-compliance for any specific parameter, mention the offered specification:
Features and Technical parameters of the system shall be as follows:
	2.6 kVA Solar Complete System – Technical Compliance Table

	1. SOLAR PANELS
	Sr.No.
	Specifications
	Value
	Bidders Offered
Specification

	
	1
	Wattage
	580 W or above (higher wattage preferred)
	

	
	2
	Type
	Mono Crystalline, N-type PERC
	

	
	3
	Number of Cells
	144 or above
	

	
	4
	Weight
	≤ 29 kg
	

	
	5
	Temperature Coefficient
(Pmax)
	-0.29%/°C
	

	
	6
	Module Voltage Rating
	1500 V
	

	
	7
	Maximum Series Fuse
Rating
	25 A
	

	
	8
	Product Workmanship
Warranty
	12 years
	

	
	9
	Power Output Warranty
	25 years
	

	
	10
	Product Certifications
	IEC 61215, IEC 61730, ISO 9001, ISO 14001,
OHSAS 18001
	

	
	11
	Frame & Junction Box
	Anodized aluminum frame, IP68 junction
box
	

	
	12
	Connector Type
	MC4 compatible
	

	
	13
	Operating Temperature
	-40 °C to +85 °C
	

	
	14
	Maximum System
Voltage
	1500 V DC
	

	
	15
	Front/Back Glass
	High-transparency tempered glass, anti-
reflective
	

	
		Brand Name (To be Filled by Bidder)



	Model No. (To be Filled by Bidder)




	2.INVERTER
	1
	Rated Output
	 2600 W, 230 VAC ± 5 %, pure sine wave.
	

	
	2
	Frequency
	50 Hz ± 5 %, auto-sensing 50/60 Hz.
	

	
	3
	Peak Efficiency
	≥ 95 % PV to inverter
	

	
	4
	Surge Capacity
	≥ 5000 VA (≥ 2× rated) for at least 5 s
	

	
	5
	Battery Support
	24 VDC bank with equalization and BMS
compatibility.
	

	
	6
	Solar Input (MPPT)
	30–400 VDC, minimum 90 A charge current
	

	
	7
	AC Charging Current
	≥ 70 A
	

	
	8
	Protection & Durability
	IP54 minimum, with overload, short circuit, over/under voltage protection
	

	
	9
	Monitoring & Communication
	Full remote monitoring (Wi Fi/RS232/RS485/CAN) and BMS support
	

	
	10
	Warranty
	Minimum 5 years total (2 years product +
3 years’ service).
	

	
	11
	Environmental
	Operating temperature −10 °C to 50 °C,
humidity 5–95 % non-condensing.
	

	
	
	Brand Name (To be Filled by Bidder)



	Model No. (To be Filled by Bidder)




	3. SOLAR PANEL MOUNTING STRUCTURE (L2 TYPE)
	1
	Structure Type
	L2 solar panel mounting structure for
rooftop installation
	

	
	2
	Material Options
	Hot-dip galvanized steel (minimum 14 gauge, ≥80 µm zinc coating) or extruded aluminum profiles; must be corrosion- resistant
	

	
	3
	Panel Compatibility
	Panels up to 650 W each
	

	
	4
	Mechanical Load Rating
	Front ≥ 5400 Pa, Rear ≥ 2400 Pa; designed to withstand minimum 150 km/h wind load
	

	
	5
	Fasteners & Hardware
	All nuts, bolts, washers, clamps must be stainless steel (SS304) or equivalent
	

	
	6
	Finish
	Steel: galvanization as above; Aluminum: anodized or equivalent corrosion protection
	

	
	7
	Installation
	Suitable for panels to be installed at specified tilt angles and series/parallel layout per system design
	

	
	8
	Durability & Life
	Designed for minimum 25-year service life under normal rooftop solar conditions
	

	
	9
	Compliance / Standards
	Comply with national & international structural and solar installation standards; workmanship to ensure corrosion protection and structural stability
	

	
	 
 Brand Name (To be Filled by Bidder)



	4. BATTERY
	1
	Battery Type
	Deep-cycle tubular lead-acid
	

	
	2
	Nominal Voltage
	12 V per battery (24V system configuration)
	

	
	3
	Minimum Capacity (Ah @
20 hr)
	150–160 Ah
	

	
	4
	Cycle Life
	≥ 900 cycles
	

	
	5
	Design Features
	Tall tubular plates, low self-discharge,
corrosion-resistant
	

	
	6
	Warranty
	12 months
	

	
	7
	Operating Temperature
	−10 °C to +50 °C
	

	
	8
	Maintenance
	Low maintenance; periodic water top-up
	

	
	 
	Brand Name (To be Filled by Bidder)



	Model No. (To be Filled by Bidder)




	5.DC CABLES
	1
	6 mm² XLPE/PVC insulated, tin-coated pure copper conductor
	

	
	2
	Rated for 1,000 V DC (suitable for PV array)
	

	
	3
	Minimum temperature rating: 90 °C
	

	
	4
	Flame retardant and UV resistant
	

	
	Brand Name (To be Filled by Bidder)

	6. AC CABLES
	1
	Suitable for AC output of inverter to DB connection
	

	
	2
	Example rating: 3-core 4 mm² or 3/29 standard
	

	
	3
	Copper conductor, PVC insulation
	

	
	4
	Rated for 230 V AC, 50 Hz
	

	
	5
	Flame retardant and UV resistant
	

	
	Brand Name (To be Filled by Bidder)

	7. DC/AC Protection Set (MCB, SPD, Isolators, Connectors)
	1
	Distribution Board (DB): Properly sized for 2.6 kW inverter output, with
space for MCBs and surge protection.
	

	
	2
	MCB / MCCB: Adequate rating for inverter AC output and load
protection; thermal-magnetic type.
	

	
	3
	Surge Protection Device (SPD): Type II SPD to protect inverter &
connected loads.
	

	
	4
	MC4 Connectors: For PV array connections; rated for 1,000 V DC, IP67,
UV resistant.
	

	










88.Electrical Installation
	1
	All wiring and connections must comply with IEC / NECA / local electrical
safety standards
	



           INSTRUCTIONS FOR PREPARING TECHNICAL BID
These Instructions are being given for strict compliance by the Bidders. Failure to fulfill any instruction given here-under may result in dis-qualification of the Bid/s.
Proposals shall be prepared on following lines: -
1. Sealed Envelope containing the Technical Proposal should clearly state:
a. “Name of Bidder	”
b. “Name of Tender	”
c. “TECHNICAL PROPOSAL”
2. The portion of Technical Proposal of this bidding document duly filled, supported with Bidder’s covering Letter and the technical Bid on Bidders Letter Head be attached as the Technical Proposal.
3. Technical Proposal shall be prepared keeping in view the specifications provided in the Data Sheet and the schedule of requirements or otherwise as placed demand further during the bidding process.
4. Following information should be attached/contained in the Technical Proposal: -
a. Receipt of payment of bidding Document Fee May be in terms of Pay Order in favor of PPHI BALOCHISTAN.
b. Completion time/Delivery time, which means; actual execution time for the titled Work.
c. Documentary evidence of fulfillment of eligibility criteria for Bidders as required by the Peoples Primary Healthcare Initiative, Balochistan. (PPHI-Balochistan).
d. Documentary evidence of fulfillment of complete schedule of requirements as per evaluation criteria including technical, administrative and service requirements of the Peoples Primary Healthcare Initiative, Balochistan (PPHI-Balochistan)
e. Description of status as Partnership / authorization from the Firm / authorized importer / distributor / manufacturer / retailer etc. (as the case may be) as required by the People’s Primary Healthcare Initiative, Balochistan (PPHI-Balochistan) in the schedule of requirements.
f. Defect Liability Period: details. (As applicable) as required by the Peoples Primary Healthcare Initiative, Balochistan (PPHI-Balochistan) in the schedule of requirements as mentioned.
g. Every page of the Bid must be numbered, signed & stamped by the authorized representative.
5. Attachment of any document not demanded by the Peoples Primary Healthcare Initiative (PPHI- Balochistan) at instruction 4 of “Instruction for preparation of Technical Bid” is strictly prohibited.
Evaluation Criteria: Selection of the successful bidder shall be based on the Single Stage-Two Envelop Method
The procedure shall be applied as follows: -
1. Bidders Eligibility Assessment. Initial evaluation of the technical proposals shall be carried-out by the PROCUREMENT COMMITTEE, as per the requirements of the eligibility criteria laid down under the heading of “Letter of Invitation for Bids – Eligibility Criteria for Bidders” in the following manner:
i. Firm must score “YES” in all requirements of the eligibility criteria to be categorized as Eligible. “NO” to any requirement of the eligibility criteria, by any bidder shall render the Firm as Ineligible.
ii. Subsequent upon said assessment, Bidders shall be categorized as:
1. Eligible Bidders
2. Ineligible Bidders

2.  ​ Return of Financial Proposals from Ineligible Bidders. Proposals from Ineligible Bidders shall be
declared “Non-Responsive”, consequently shall NOT be accepted for any further evaluation:
iii. Their Financial Proposals shall be returned without being opened.
iv. Their Bid security shall be released upon their written request.
3.  ​ Return of Non-Responsive Proposals & preparation of Technical Evaluation Report. Technical Proposals not conforming to the required technical, administrative or legal requirements shall be declared as “Non-Responsive” and consequently shall NOT be accepted for any further evaluation:
i. Their financial proposals shall be returned without being opened.
ii. Their Bid security shall be released upon their written request.
iii. Technical Evaluation Report, shall be prepared duly signed by all the members of the Procurement Committee, giving REASONS for;
1. Acceptance of the Eligible & Responsive Bid/s and.
2. Rejection of the Ineligible &/OR Non-Responsive Bid/s.
iv. Technical Evaluation concludes at this stage.
        4. Recommendation of Procurement Committee

After Technical Qualification, the contract will be awarded to the “Lowest Financially Evaluated bidder” with minimum quoted rates among all the Technical qualified Contractors.


Note


BID GRIEVENCES

Any bidder having a grievance relating to the tender process, including technical evaluation, financial evaluation, bid responsiveness, qualification, sample assessment, or bid comparison, shall submit the grievance in writing to the Chief Executive Officer, PPHI-Balochistan, for onward submission to the Grievance Redressal Committee, within five (05) working days from the date of issuance/communication of the relevant evaluation result and, in any case, prior to the award of contract. Any grievance received after the prescribed period or after the award of contract shall not be entertained. Failure to submit a grievance within the stipulated time shall constitute a waiver of the bidder's right to challenge the procurement proceedings before the Procuring Agency.
	
[image: ]The Head Office,
People’s Primary Healthcare Initiative, Balochistan.
Admin Section
Ref No. PPHI-B/H.O-BLN/SOLAR/2026-27/01
Dated: 	

Financial Proposal
People’s Primary Healthcare Initiative (PPHI) - Balochistan


Bidding Document for Supply, Installation and commissioning of Solar Step-Up Systems at 157 Basic Health Units (BHUs), Across Balochistan.




NAME OF BIDDER: 	
(To be filled-in by the Bidder)





Address: Peoples Primary Healthcare Initiative (PPHI) Balochistan House # 8-A, Jinnah Town Samungli Road, Quetta-Pakistan.

                                                                 Phone: 081-2863620
              Website: www.pphib.org

1. Name of company: 	

2. Complete Postal Address: 	




3. Tel No:	4. Email address:	


5.	Fax No: 	6. Mobile No: 	


2.  Authorized Representative’s name & designation:



8. Type of Business:
(1) Sole Proprietorship	□	(2)	Partnership	□
(3)	Corporation (Private Ltd.) □	(4)	Corporation (Public Ltd) □

9. National Tax Number& Date of issuance: _	


10. Sales Tax Registration No. / BRA Registration No.	

11. GST No. 	


12. Bid Validity: 	(Please specify in No. of Days)

13. Total Bid Value: 	(In Pakistani Rupees)

INSTRUCTIONS FOR PREPARING FINANCIAL PROPOSAL
These Instructions are being given for strict compliance by the Bidders. Failure to fulfill any instruction given here-under may result in disqualification of the Bid/s.
Financial Proposals shall be prepared on following lines: -
1. Sealed Envelope containing the Financial Proposal should clearly state:
a. “Name of Bidder	”
b. “Name of Tender	”
c. “Financial Proposal”
2. The portion of Financial Proposal of this bidding document duly filled, supported with Bidder’s
covering Letter be attached as the Financial Proposal of the bidder.
3. Following information should be attached/contained in the financial proposal: -
a. Original Bid Security (If required by the Peoples Primary Health Initiative (PPHI- Balochistan).
b. Taxes must be included along-with the price of each item.
c. Financial Bid shall be prepared on the Bidders Letter Head in the BOQs format attached in tender and needs to be provide in the financial proposal.
SUMMARY OF BID PRICES FOR LOT 01
	LOT
No.
	
Description
	
Facility Type
	System Size
	No. Of
Sites
	Unit Price Per System (PKR)
	Total Price
(PKR)

	               Lot1
	Supply & Installation of Solar Step-Up
Systems Complete
	BHU
	2.6 kVA
	30
	
	

	Total
	

	FINACIAL SUMMARY OF LOT 1

	DISCRIPTION
	AMOUNT

	Total Cost of Lot-1 (Without Tax)
	

	Total Cost of Lot-1 (Including Tax)
	


SUMMARY OF BID PRICES FOR LOT 02
	Item No.
	
Description
	
Facility Type
	System Size
	No. Of Sites
	Unit Price Per System (PKR)
	Total Price
(PKR)

	               Lot2
	Supply & Installation of Solar Step-Up
Systems Complete
	BHU
	2.6 kVA
	24
	
	

	Total
	

	FINACIAL SUMMARY OF LOT 2

	DISCRIPTION
	AMOUNT

	Total Cost of Lot-2 (Without Tax)
	

	Total Cost of Lot-2 (Including Tax)
	


SUMMARY OF BID PRICES FOR LOT 03
	LOT
No.
	
Description
	
Facility Type
	System Size
	No. Of Sites
	Unit Price Per System (PKR)
	Total Price
(PKR)

	               Lot3
	Supply & Installation of Solar Step-Up
Systems Complete
	BHU
	2.6 kVA
	    13
	
	

	Total
	

	FINACIAL SUMMARY OF LOT 3

	DISCRIPTION
	AMOUNT

	Total Cost of Lot-3 (Without Tax)
	

	Total Cost of Lot-3 (Including Tax)
	



	

SUMMARY OF BID PRICES FOR LOT 04
	LOT
No.
	
Description
	
Facility Type
	System Size
	No. Of
Sites
	Unit Price Per System (PKR)
	Total Price (PKR)

	
Lot4
	Supply & Installation of Solar Step-
Up Systems complete
	BHU
	2.6 kVA
	28
	
	

	Total
	

	FINACIAL SUMMARY OF LOT 4

	DISCRIPTION
	AMOUNT

	Total Cost of Lot-4 (Without Tax)
	

	Total Cost of Lot-4 (Including Tax)
	


SUMMARY OF BID PRICES FOR LOT 05
	LOT
No.
	
Description
	
Facility Type
	System Size
	No. Of
Sites
	Unit Price Per System (PKR)
	Total Price (PKR)

	
Lot5
	Supply & Installation of Solar Step-
Up Systems complete
	BHU
	2.6 kVA
	31
	
	

	Total
	

	FINACIAL SUMMARY OF LOT 5

	DISCRIPTION
	AMOUNT

	Total Cost of Lot-5 (Without Tax)
	

	Total Cost of Lot-5 (Including Tax)
	


SUMMARY OF BID PRICES FOR LOT 06
	Item No.
	
Description
	
Facility Type
	System Size
	No. Of
Sites
	Unit Price Per System (PKR)
	Total Price (PKR)

	
Lot6
	Supply & Installation of Solar Step-
Up Systems complete
	BHU
	2.6 kVA
	15
	
	

	Total
	

	FINACIAL SUMMARY OF LOT 6

	DISCRIPTION
	AMOUNT

	Total Cost of Lot-6 (Without Tax)
	

	Total Cost of Lot-6 (Including Tax)
	


SUMMARY OF BID PRICES FOR LOT 07
	LOT
No.
	
Description
	
Facility Type
	System Size
	No. Of
Sites
	Unit Price Per System (PKR)
	Total Price (PKR)

	Lot7
	Supply & Installation of Solar Step-Up
Systems
	BHU
	2.6 kVA
	16
	
	

	Total
	

	FINACIAL SUMMARY OF LOT 7

	DISCRIPTION
	AMOUNT

	Total Cost of Lot-7 (Without Tax)
	

	Total Cost of Lot-7 (Including Tax)
	



BOQ for Supply, Installation, Testing & Commissioning of Solar Systems – Lot 1
	BOQ For Supply, Installation G Commissioning of 2.6 kVA Solar Systems at designated Locations

	Sr. No
	Product / Description
	Unit
	Qty per Site
	No. of Sites
	Total Qty
	Unit Price (PKR)
	Tax BRA/GST
%
	Tax BRA/GST
Amount
	Total Amount With Tax

	1
	Solar Pannels
	No.
	6
	30
	180
	
	
	
	

	2
	Inverter
	Each
	1
	30
	30
	
	
	
	

	3
	Solar Pannels
Mounting Structure (L2 Type)
	Set
	3
	30
	90
	
	
	
	

	4
	Battery Bank
	No.
	2
	30
	60
	
	
	
	

	5
	DC Cabels
	Meter
	30
	30
	900
	
	
	
	

	6
	AC Cables
	Meter
	25
	30
	750
	
	
	
	

	
7
	DC/AC Protection Set (MCB, SPD,
Isolators,
Connectors)
	
Job
	
1
	30
	30
	
	
	
	

	8
	Electrical
Installation
	Job
	1
	30
	30
	
	
	
	

	Total Cost in PKR without Tax
	

	Tax Amount
	

	Grand Total Cost in PKR with Tax
	
































BOQ for Supply, Installation, Testing & Commissioning of Solar Systems – Lot 2
	BOQ For Supply, Installation G Commissioning of 2.6 kVA Solar Systems at designated Locations

	Sr. No
	Product / Description
	Unit
	Qty per Site
	No. of Sites
	Total Qty
	Unit Price (PKR)
	Tax BRA/GST
%
	Tax BRA/GST
Amount
	Total Amount With Tax

	1
	Solar Pannels
	No.
	6
	24
	144
	
	
	
	

	2
	Inverter
	Each
	1
	24
	24
	
	
	
	

	3
	Solar Pannels
Mounting Structure (L2 Type)
	Set
	3
	24
	72
	
	
	
	

	4
	Battery Bank
	No.
	2
	24
	48
	
	
	
	

	5
	DC Cabels
	Meter
	30
	24
	720
	
	
	
	

	6
	AC Cables
	Meter
	25
	24
	600
	
	
	
	

	
7
	DC/AC Protection Set (MCB, SPD,
Isolators,
Connectors)
	
Job
	
1
	24
	24
	
	
	
	

	8
	Electrical
Installation
	Job
	1
	24
	24
	
	
	
	

	Total Cost in PKR without Tax
	

	Tax Amount
	

	Grand Total Cost in PKR with Tax
	
































BOQ for Supply, Installation, Testing & Commissioning of Solar Systems – Lot 3
	BOQ For Supply, Installation G Commissioning of 2.6 kVA Solar Systems at designated Locations

	Sr. No
	Product / Description
	Unit
	Qty per Site
	No. of Sites
	Total Qty
	Unit Price (PKR)
	Tax BRA/GST
%
	Tax BRA/GST
Amount
	Total Amount With Tax

	1
	Solar Pannels
	No.
	6
	13
	78
	
	
	
	

	2
	Inverter
	Each
	1
	13
	13
	
	
	
	

	3
	Solar Pannels
Mounting Structure (L2 Type)
	Set
	3
	13
	39
	
	
	
	

	4
	Battery Bank
	No.
	2
	13
	26
	
	
	
	

	5
	DC Cabels
	Meter
	30
	13
	390
	
	
	
	

	6
	AC Cables
	Meter
	25
	13
	325
	
	
	
	

	
7
	DC/AC Protection Set (MCB, SPD,
Isolators,
Connectors)
	
Job
	
1
	13
	13
	
	
	
	

	8
	Electrical
Installation
	Job
	1
	13
	13
	
	
	
	

	Total Cost in PKR without Tax
	

	Tax Amount
	

	Grand Total Cost in PKR with Tax
	
































BOQ for Supply, Installation, Testing & Commissioning of Solar Systems – Lot 4
	BOQ For Supply, Installation G Commissioning of 2.6 kVA Solar Systems at designated Locations

	Sr. No
	Product / Description
	Unit
	Qty per Site
	No. of Sites
	Total Qty
	Unit Price (PKR)
	Tax BRA/GST
%
	Tax BRA/GST
Amount
	Total Amount With Tax

	1
	Solar Pannels
	No.
	6
	28
	168
	
	
	
	

	2
	Inverter
	Each
	1
	28
	28
	
	
	
	

	3
	Solar Pannels
Mounting Structure (L2 Type)
	Set
	3
	28
	84
	
	
	
	

	4
	Battery Bank
	No.
	2
	28
	56
	
	
	
	

	5
	DC Cabels
	Meter
	30
	28
	840
	
	
	
	

	6
	AC Cables
	Meter
	25
	28
	700
	
	
	
	

	
7
	DC/AC Protection Set (MCB, SPD,
Isolators,
Connectors)
	
Job
	
1
	28
	28
	
	
	
	

	8
	Electrical
Installation
	Job
	1
	28
	28
	
	
	
	

	Total Cost in PKR without Tax
	

	Tax Amount
	

	Grand Total Cost in PKR with Tax
	
































BOQ for Supply, Installation, Testing & Commissioning of Solar Systems – Lot 5
	BOQ For Supply, Installation G Commissioning of 2.6 kVA Solar Systems at designated Locations

	Sr. No
	Product / Description
	Unit
	Qty per Site
	No. of Sites
	Total Qty
	Unit Price (PKR)
	Tax BRA/GST
%
	Tax BRA/GST
Amount
	Total Amount With Tax

	1
	Solar Pannels
	No.
	6
	31
	186
	
	
	
	

	2
	Inverter
	Each
	1
	31
	31
	
	
	
	

	3
	Solar Pannels
Mounting Structure (L2 Type)
	Set
	3
	31
	93
	
	
	
	

	4
	Battery Bank
	No.
	2
	31
	62
	
	
	
	

	5
	DC Cabels
	Meter
	30
	31
	930
	
	
	
	

	6
	AC Cables
	Meter
	25
	31
	775
	
	
	
	

	
7
	DC/AC Protection Set (MCB, SPD,
Isolators,
Connectors)
	
Job
	
1
	31
	31
	
	
	
	

	8
	Electrical
Installation
	Job
	1
	31
	31
	
	
	
	

	Total Cost in PKR without Tax
	

	Tax Amount
	

	Grand Total Cost in PKR with Tax
	
































BOQ for Supply, Installation, Testing & Commissioning of Solar Systems – Lot 6
	BOQ For Supply, Installation G Commissioning of 2.6 kVA Solar Systems at designated Locations

	Sr. No
	Product / Description
	Unit
	Qty per Site
	No. of Sites
	Total Qty
	Unit Price (PKR)
	Tax BRA/GST
%
	Tax BRA/GST
Amount
	Total Amount With Tax

	1
	Solar Pannels
	No.
	6
	15
	90
	
	
	
	

	2
	Inverter
	Each
	1
	15
	15
	
	
	
	

	3
	Solar Pannels
Mounting Structure (L2 Type)
	Set
	3
	15
	45
	
	
	
	

	4
	Battery Bank
	No.
	2
	15
	30
	
	
	
	

	5
	DC Cabels
	Meter
	30
	15
	450
	
	
	
	

	6
	AC Cables
	Meter
	25
	15
	375
	
	
	
	

	
7
	DC/AC Protection Set (MCB, SPD,
Isolators,
Connectors)
	
Job
	
1
	15
	15
	
	
	
	

	8
	Electrical
Installation
	Job
	1
	15
	15
	
	
	
	

	Total Cost in PKR without Tax
	

	Tax Amount
	

	Grand Total Cost in PKR with Tax
	
































BOQ for Supply, Installation, Testing & Commissioning of Solar Systems – Lot 7
	BOQ For Supply, Installation G Commissioning of 2.6 kVA Solar Systems at designated Locations

	Sr. No
	Product / Description
	Unit
	Qty per Site
	No. of Sites
	Total Qty
	Unit Price (PKR)
	Tax BRA/GST
%
	Tax BRA/GST
Amount
	Total Amount With Tax

	1
	Solar Pannels
	No.
	6
	16
	96
	
	
	
	

	2
	Inverter
	Each
	1
	16
	16
	
	
	
	

	3
	Solar Pannels
Mounting Structure (L2 Type)
	Set
	3
	16
	48
	
	
	
	

	4
	Battery Bank
	No.
	2
	16
	32
	
	
	
	

	5
	DC Cabels
	Meter
	30
	16
	480
	
	
	
	

	6
	AC Cables
	Meter
	25
	16
	400
	
	
	
	

	
7
	DC/AC Protection Set (MCB, SPD,
Isolators,
Connectors)
	
Job
	
1
	16
	16
	
	
	
	

	8
	Electrical
Installation
	Job
	1
	16
	16
	
	
	
	

	Total Cost in PKR without Tax
	

	Tax Amount
	

	Grand Total Cost in PKR with Tax
	
































Note: Each Bidder must mention clearly the rate of BRA & GST applicable on each item of its Bid.
4. Offer must be quoted on TCA (Total Cost of Acquisition) basis at the risk & cost of the bidder. This means:
i. ALL costs (including duties, taxes & other Govt. payables) incurred up-to delivery at the designated location of the Peoples Primary Health Initiative (PPHI-B).
ii. Complete services as required in the schedule of requirements of this bidding document.
iii. Cost including fixation, assembling, dismantling etc. (As & where applicable).
5. BST/GST Taxes must be included along-with the price of each item/components/service.
6. In-case of any Tax exemptions, exemption certificate from the concerned Tax Office / Regional Tax Office pertaining particularly to this case may be provided; otherwise, taxes shall be deducted as per Government Policy / Rules.
Every page of the Bid must be numbered, signed & stamped by the bidder.
7. Financial Evaluation. Financial Proposals of the Responsive Technical Proposals shall be publicly opened in the next meeting as specified in this document under the heading of “Letter of Invitation for Bid” Financial Comparative Statement / Evaluation Report of the “Responsive Proposals” shall be prepared by the PROCUREMENT COMMITTEE in the following manner:
Financial Evaluation Criteria

	Lot-1 Financial Comparative Statement

	S.#
	
System Description
	
Quantity
	
Unit (Sites)
	Qualified
Bidder 1
	Qualified
Bidder 2
	Qualified
Bidder 3

	
	
	
	
	Unit Price
	Total Price
	Unit Price
	Total Price
	Unit Price
	Total Price

	1
	2.6 kVA Solar
System
	xxxx
	xxxx
	xxxx
	xxxx
	xxxx
	xxxx
	xxxx
	xxxx

	Total Evaluated Cost (Lot-1)
	
	
	


Lot-2-8 Financial Comparative Statement
(same format repeated)


Moreover;


i. Subsequently, the prepared Financial Evaluation Report shall duly be signed by all the members of the Procurement Committee.
ii. Comparatives of Financial will be prepared and signed by the procurement Committee in detail.
iii. If there is any discrepancy between Unit rate and total rate, the unit rate will always govern.
iv. If there is any discrepancy in tender documents clause and Work Order Clause, the work order Clause will always govern.
v. If there is any discrepancy between amount in words and amount in figures, the amount in words will always govern.
vi. All prices shall quote along with all applicable taxes and all quoted prices will be considered inclusive of all applicable taxes

Recommendation of Procurement Committee
I- After Financial Evaluation (of only technically approved bidders), the contract will be awarded to the “Lowest Financially Evaluated bidder” with minimum quoted rates among all the Technical Qualified Bidders. PPHI-B reserve the right to issue work order to the lowest quoted bidder on items wise or as whole of the finically evaluated Bid
II- PPHI-Balochistan reserves the right to award complete work as per mentioned as detailed in data sheet of assignment of this document or partially as this shall be subject to availability of funds.
TERMS AND CONDITIONS:
1. Completion time may be clearly specified. Where completion time shall mean; time consumed execution of required services to the designated location of Peoples Primary Health Initiative (PPHI-B), including but not limited to time required for development of Performa/forms (Complete delivery as per the schedule of requirements services detailed in the Data-Sheet)
2. Maximum completion time for the assignment is 45 Days from the date of work Order.
3. Tenders must be quoted in Pakistani Rupees (PKR).
4. Tax Liability:
i. Complete Tax liability is to be borne by the Vendor/individual as per the applicable rate of tax authority.
ii. Quoted prices shall be inclusive of all applicable Taxes with maintaining of %age ofBRA/ GST.
iii. In-case of any Tax exemptions, exemption certificate from the concerned Tax Office / Regional Tax Office pertaining particularly to this case may be provided; otherwise, taxes shall be deducted as per Government Policy / Rules.
iv. All tax variations by the Tax Authorities will be borne by the vendor only, there will be no change in contract.
5. Validity of the bid would be at-least 60 Days (to be specified by the Peoples Primary Health Initiative (PPHI-Balochistan) / office) from the date of Tender opening.
6. Financial Bids must be accompanied with Bid Security Deposit at Call from a scheduled bank @ 2% of quoted bid value favoring the PPHI Balochistan.
7. In case of late delivery of supplies, the bidder may be blacklisted and late delivery penalty (Liquidated Damages) shall be imposed at the rate of 0.25% per day (of the value of items delivered late) per day, up to a maximum of 20% of the Contract Value.
8. Bid Security of successful bidder/s shall be released after 30 days of completion of all deliveries as per work/supply order.
9. A performance security equivalent to 5% of the contract value, in the form of a Pay Order or Demand Draft, shall be required to cover the warranty period (only for warranty items if any).
10. The bid security of successful bidders submitted by the firm shall be considered as performance security. However, if the firm/vendor opts, a separate Bid Security amounting to 2% of the total work/supply order value in lieu of total bid security or performance Security.
11. Bid Security of unsuccessful bidder/s shall be released within 10 working days from the date of award of contract to the successful bidder/s.
12. Tender will be awarded to the technically qualified (with approved sample) lowest quoted bidder (Item-wise or whole) after financial evaluation.
13. PPHI-Balochistan shall not be responsible for any theft or loss during delivery of supplies at required destination.
14. Payment release is subject to delivery report duly signed by the authorized officials by competent authority PPHI-Balochistan.
15. Payment:
i. Advance payment is not allowed.
ii. Partial payment shall be made upon successful supply of 50% of the total ordered items. Payment for 50% of the supplied quantity will be processed, while 10% shall be withheld as performance security until completion of the remaining supplies. The balance payment will be released upon 100% successful delivery of the remaining items within 30 working days subject to the submission of all required documents and verification of quality as per the specifications outlined in the tender documents and approved samples.
CURRENCY & BID VALIDITY
· Pak Rupees & 60 Days
































DECLARATION BY THE BIDDER
I solemnly undertake that:

a. Having read, understood & made myself aware of all the Terms & conditions mentioned in this Bidding Document & the Rules, Regulations & Policies of the Government of Balochistan, governing the procurement & financial matters, AGREE, ACCEPT & UNDETAKE TO ABIDE BY THE SAME.
b. The information provided in this form is correct to the best of my knowledge & in the event of change; details will be provided as soon as possible

Name & Designation 	

Signature 	Date 	
           Company Stamp. ___________________________________________
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